## 0. Read Me
Forty questions on The Data Center Development Handbook
Answer in the yellow column of sheet 1. Numbers as numbers, in the unit the question asks for (a ratio as 1.70, a percentage as 8.9). Multiple-choice as a single letter.
Column F marks each answer as you type. Sheet 2 counts your errors chapter by chapter: that is your revision list.
Sheet 3 carries every answer and the reason for it. Nothing is hidden. Read it after you have answered, not before.
The numeric questions use the book's own campus, its power and its underwrite. The figures come from the four companion workbooks; three come from the three cases.
julianrsterling.com/datacenter

## 2. Score
Chapter | Questions | Answered | Right | Wrong
Sites and screening | 4 | 0 | 0 | 0
Power and the utility | 8 | 0 | 0 | 0
Underwriting | 16 | 0 | 0 | 0
Execution | 4 | 0 | 0 | 0
Cases | 8 | 0 | 0 | 0
Total | 40 | 0 | 0 | 0
Score
Revise first

## 1. Questions
# | Chapter | Question | Your answer | Marked
1 | Sites and screening | In the Appendix A scorecard, hard fails are: A) tested first, pass or fail, with no weight B) optional C) weighted like any criterion D) scored 1 to 5
2 | Sites and screening | A criterion you have not verified should be scored: A) 5 B) 1 C) 3 D) as unknown, never as a middling 3
3 | Sites and screening | Weight of the power and connectivity group in the Appendix A scorecard, in per cent?
4 | Sites and screening | Two sites score 82 and 78. The 82 rests on four criteria marked unknown; the 78 is fully verified. Which ranks higher? A) the 82 B) neither C) the 78, ranked on verified score D) they are tied
5 | Power and the utility | A ratchet provision: A) sets billing demand at a percentage of the highest recorded peak for months afterward B) is a fuel clause C) refunds CIAC D) caps the demand charge
6 | Power and the utility | Contract demand is: A) the peak B) the capacity the utility commits to make available and plan around C) the IT load D) what you pay on
7 | Power and the utility | Demand charge of $12 a kW-month on a 100 MW peak: the monthly demand charge, in $m? (one decimal)
8 | Power and the utility | At a 95% load factor, that charge per MWh, in dollars? (one decimal)
9 | Power and the utility | At a 30% load factor, per MWh, in dollars? (nearest whole number)
10 | Power and the utility | Under ERCOT's four coincident peak methodology, transmission cost for large loads is allocated on: A) contract demand B) demand in the four fifteen-minute intervals of highest system demand, June to September C) the ratchet D) annual energy
11 | Power and the utility | Contribution in aid of construction is: A) a tax credit B) the demand charge C) the customer's up-front payment toward facilities the utility will own D) a rent deposit
12 | Power and the utility | Chapter 7 frames on-site generation as: A) a destination B) usually a bridge, rarely a destination C) always cheaper than the grid D) a permanent power plant
13 | Underwriting | Turnkey: 180 MW at $11m a MW. Capital cost, in $m?
14 | Underwriting | Turnkey gross rent at $105 a kW-month on 180 MW, a year, in $m? (one decimal)
15 | Underwriting | Turnkey yield on cost, NOI of 215m on 1,980m, in per cent? (one decimal)
16 | Underwriting | Turnkey stabilised value at a 7.75% exit cap, in $m? (nearest whole number)
17 | Underwriting | Turnkey spread of yield on cost over the exit cap, in basis points? (nearest whole number)
18 | Underwriting | Powered shell: 180 MW at $5m, NOI 92m. Yield on cost, in per cent? (one decimal)
19 | Underwriting | Powered land: 240 acres at $15,000 plus $8m of pre-development. Basis, in $m? (one decimal)
20 | Underwriting | Multiple on the powered-land winners? (two decimals)
21 | Underwriting | Break-even hit rate for the powered-land business, in per cent? (one decimal)
22 | Underwriting | Appendix G: levered return in the base case, 3% escalator, in per cent? (one decimal)
23 | Underwriting | Levered return on flat rent, in per cent? (one decimal)
24 | Underwriting | Against the 3% escalator base case, a twelve-month energisation slip costs how many basis points of levered return? (nearest 5)
25 | Underwriting | Against the same base, the correlated case costs how many basis points? (nearest whole number)
26 | Underwriting | Capital call in the twelve-month delay, in $m? (one decimal)
27 | Underwriting | One point of rent escalator over a fifteen-year lease is worth what share of face rent, in per cent? (one decimal)
28 | Underwriting | Construction interest rate implied by the chapter's $75m of extra interest on a drawn balance of $1,188m, in per cent? (one decimal)
29 | Execution | What determines energisation, per Chapter 14? A) the lease signing B) the permit C) the notice to proceed D) the purchase order date for long-lead equipment
30 | Execution | Appendix D: upper end of the quoted lead time for substation power transformers of 5 to 50 MVA, in weeks?
31 | Execution | Large gas turbines in the lead-time tracker: A) 12 weeks B) always available C) 40 weeks D) carry no number: get a written slot date or assume you cannot have one
32 | Execution | Appendix C: anything older than ninety days should be: A) re-dated before it goes into an investment memo B) ignored C) sent to counsel D) deleted
33 | Cases | Case one: a full-load commissioning test at 180 MW with an 80% ratchet. Billing demand from month 2, in MW?
34 | Cases | Case one: demand charges paid on unused capacity after the test month, in $m? (two decimals)
35 | Cases | Case one: months in which the ratchet sets the bill?
36 | Cases | Case two: months of rent the bridge buys in the chapter's gap?
37 | Cases | Case two: value of bridging on the illustrative costs, in $m? (nearest whole number)
38 | Cases | Case two: bridge power cost at which bridging stops paying, in $ per MWh? (nearest whole number)
39 | Cases | Case three: minimum take bill a month, 80% of 180 MW at $12, in $m? (two decimals)
40 | Cases | Case three: expected cost of the five-year tail at signing, in $m? (one decimal)

## 3. Marking
# | Chapter | Type | Answer | Tolerance | Why
1 | Sites and screening | mcq | A |  | A condition that can kill a site should never be outvoted by criteria that cannot.
2 | Sites and screening | mcq | D |  | A 3 launders ignorance into data.
3 | Sites and screening | num | 45 | 0.5 | The largest group by far.
4 | Sites and screening | mcq | C |  | Treat unknowns as scheduled work, not neutral values.
5 | Power and the utility | mcq | A |  | 80 or 90 per cent is typical, for eleven months.
6 | Power and the utility | mcq | B |  | Billing demand is what you actually pay on.
7 | Power and the utility | num | 1.2 | 0.05 | Chapter 8.
8 | Power and the utility | num | 17.5 | 0.2 | About 68,400 MWh in a thirty-day month.
9 | Power and the utility | num | 55 | 1 | Same tariff, same peak, different business.
10 | Power and the utility | mcq | B |  | A flat load cannot avoid them.
11 | Power and the utility | mcq | C |  | Generally taxable to the utility, so expect a gross-up.
12 | Power and the utility | mcq | B |  | Assets bought as a bridge are sized, contracted and financed differently.
13 | Underwriting | num | 1980 | 0.5 | Appendix G.
14 | Underwriting | num | 226.8 | 0.1 | "About 227m".
15 | Underwriting | num | 10.9 | 0.05 | 10.86%.
16 | Underwriting | num | 2774 | 1 | "About 2,770m".
17 | Underwriting | num | 311 | 1 | "310".
18 | Underwriting | num | 10.2 | 0.05 | Against a 7.5% exit cap.
19 | Underwriting | num | 11.6 | 0.05 | Sold at $250,000 a MW, 45m.
20 | Underwriting | num | 3.88 | 0.01 | "Close to fourfold".
21 | Underwriting | num | 25.8 | 0.1 | Below one site in four, a near-fourfold multiple loses money.
22 | Underwriting | num | 22.6 | 0.1 | The chapter's "high teens" is the flat-rent case.
23 | Underwriting | num | 18.6 | 0.1 | The assumption behind the chapter's headline number.
24 | Underwriting | num | 450 | 5 | -449.8 bp; the rent miss of 8% costs 239.
25 | Underwriting | num | 809 | 1 | Against 873 for the four effects taken one at a time: not additive.
26 | Underwriting | num | 94.8 | 0.1 | About 12% of committed equity.
27 | Underwriting | num | 7.5 | 0.1 | A 3% escalator at $105 matches a 2% escalator at $112.93.
28 | Underwriting | num | 6.3 | 0.05 | The one added input in Appendix G that is not invented.
29 | Execution | mcq | D |  | Appendix D turns that argument into a tracker.
30 | Execution | num | 110 | 1 | 75 to 110 weeks, 2026 quotes.
31 | Execution | mcq | D |  | Sold out into multi-year queues.
32 | Execution | mcq | A |  | One of the three habits alongside the lists.
33 | Cases | num | 144 | 0.5 | 80% of 180, while the campus draws 45.
34 | Cases | num | 4.54 | 0.01 | Phasing the test at 60 MW saves 4.5m.
35 | Cases | num | 7 | 0.5 | Months 2 to 8.
36 | Cases | num | 30 | 0.5 | Month 18 against month 48.
37 | Cases | num | 28 | 0.5 | A loss of 4.7m if the gas is nine months late.
38 | Cases | num | 117 | 1 | The margin on power is wide; the margin on time is not.
39 | Cases | num | 1.73 | 0.01 | Sixty months of it after a fifteen-year lease.
40 | Cases | num | 8.2 | 0.1 | 27.0m in the worst case.