## README
The Data Center Operations Handbook: companion workbook (Varden Point)
This workbook rebuilds the fictional 36 MW colocation campus the book follows, month by month for 36 months from handover.
Every figure the book prints about Varden Point is computed here by live formula. Blue cells on a light blue background are inputs (all on the Inputs sheet).
Everything else is a formula. There is no macro, no data table and no circular reference. Amounts are US dollars unless stated.
Sheets:
Inputs : every assumption: capacity, lease-up, prices, energy terms, PUE curve, staffing, contracts, loan, test program, retrofit.
Monthly : 36 months: sold and drawn kW, PUE by building, rent, cross-connects, services, energy billed, energy cost, energy margin, churn, commissions.
Annual : the three-year budget of Chapter 11, per-MW measures, the loan and DSCR of Chapter 15, breakevens, emissions and water.
Cooling : Chapter 5: halls conditioned as needed versus all four, warmer supply air, and the breakeven for opening a hall.
Staffing : Chapter 2: seats, FTE per seat, the organization, and the in-house, hybrid and outsourced models.
Power_SLA : Chapters 3, 4 and 7: the nines, generator test fuel, fuel autonomy, circuits, the month-7 incident and its credit.
Maintenance : Chapter 6: the preventive program in work orders and person-hours.
Capacity : Chapter 10: oversubscription and the UPS block mapping of Building B.
Pricing : Chapters 8 and 9: the price floor, the energy billing structures, the hyperscale ramp.
Retrofit : Chapter 14: suite B8, air-cooled or liquid-cooled, in the two market cases.
Checks : the book's printed figures beside the live formulas. At the default inputs every line reads OK.
How to use it:
1. Change any blue input on the Inputs sheet and every dependent figure moves (lease-up, prices, PUE terms, tariff, staffing, loan).
2. Set 'Condition all four retail halls from day one' to 1 to see the cost of opening halls before they are needed.
3. Set the utility price shock (for example 20%) to see why a pass-through business barely notices it.
4. The Checks sheet compares with the book at the DEFAULT inputs; after you change an input some checks read DIFF. That is expected.
Varden Point is fictional. Every input is an illustrative teaching assumption, not a market statistic.

## Inputs
Inputs (blue cells may be changed)
CAPACITY AND LEASE-UP
Design critical IT capacity per building (kW) | 12000
Retail hall size, Building A (kW) | 3000
Number of retail halls | 4
Building A sold kW at month 0 | 1800
Building A sold kW at month 12 | 4800
Building A sold kW at month 24 | 7800
Building A sold kW at month 36 | 9600
Building B sold kW at month 0 | 3000
Building B sold kW at month 12 | 6000
Building B sold kW at month 24 | 9000
Building B sold kW at month 36 | 10500
Building C billable kW, lease year 1 | 6000
Building C billable kW, lease year 2 | 9000
Building C billable kW, lease year 3 | 12000
Retail churn, share of sold kW per month | 0.6%
Drawn load as share of sold, Building A | 55%
Drawn load as share of sold, Building B | 65%
Drawn load as share of sold, Building C | 75%
PRICES
Price year 1, Building A ($ per kW-month) | 195
Annual escalator, Building A | 3%
Price year 1, Building B ($ per kW-month) | 135
Annual escalator, Building B | 3%
Price year 1, Building C ($ per kW-month) | 118
Annual escalator, Building C | 2.5%
Cross-connects per MW sold, Building A | 30
Cross-connect price ($ per month) | 300
Remote hands revenue ($ per MW sold per month, A and B) | 1500
ENERGY
Utility cost year 1 ($ per MWh) | 74
Utility cost escalator | 3%
Utility price shock (stress) | 0% | e.g. 20% for Chapter 11
Proportional overhead, Building A | 0.24
Proportional overhead, Building B | 0.2
Proportional overhead, Building C | 0.14
Fixed overhead per conditioned retail hall (kW) | 225
Fixed overhead, Building B (kW) | 600
Fixed overhead, Building C (kW) | 300
Condition all four retail halls from day one (1 = yes) | 0 | Chapter 5: 0 is the base case
Proportional overhead A with warmer supply air | 0.21 | Chapter 5: 20 to 24 degrees C
Retail energy multiplier (Building A) | 1.55
Wholesale PUE cap (Building B) | 1.45
Wholesale energy fee ($ per MWh of IT energy) | 5
OPERATING COSTS
Staff and security cost escalator | 3.5%
Productive hours per FTE per year | 1800
Contracted security seats (24x7) | 2
Security rate ($ per hour) | 38
Contract, repairs, tax and insurance escalator | 3%
Repairs and consumables year 1 ($) | 450000
Insurance year 1 ($) | 1100000
Property tax year 1 ($) | 2200000
Building C's share of insurance and tax | 33.33%
Audits year 1 ($) | 160000
Platform management fee (share of recurring revenue) | 3%
Commission (months of MRC per gross kW sold, A and B) | 1
Lifecycle reserve ($ per design kW per year) | 35
Water use, Building A (liters per kWh of IT energy) | 1.1
Water use, Building B (liters per kWh of IT energy) | 1.1
Water use, Building C (liters per kWh of IT energy) | 0.15
Water and sewer ($ per cubic meter) | 8
GENERATORS AND FUEL
Generators | 21
Generator rating (kW) | 3000
kWh per gallon of diesel | 14
Diesel price ($ per gallon) | 3.8
Monthly run hours per generator | 0.5
Monthly run load (share of rating) | 35%
Annual load bank hours per generator | 4
Annual load bank load (share of rating) | 75%
Fuel autonomy (hours) | 48
Facility load of one building at design (kW) | 16200
LOAN
Term loan ($) | 300000000
Interest rate | 6.4%
Amortization in year 3 (share of principal) | 3%
DSCR lock-up | 1.25
DSCR default | 1.1
EMISSIONS
Grid emission factor (tCO2e per MWh) | 0.38
Share of facility MWh under the renewable contract | 60%
kg CO2 per gallon of diesel | 10.21
PRICE FLOOR AND RETROFIT
Build cost ($ per MW) | 11000000
Required unlevered yield | 9%
Suite B8 size, block-limited (kW) | 1200
Liquid-cooling capex ($ per MW) | 3200000
Air-cooled fit-out ($) | 150000
Liquid-cooled price ($ per kW-month) | 175
Discount rate | 9%
Rent escalator after year 3 | 3%
Years | 10
Weeks of works before the liquid suite bills | 26
INCIDENT (CHAPTER 7)
Contracted kW of the affected customers | 610
Minutes without power | 11
Their price ($ per kW-month) | 195
Month of the incident | 7

## Monthly
Monthly model: 36 months from handover
Sold kW at mid-month, interpolated between the year-end values on Inputs.
Month | Year | Share of year | Sold A | Sold B | Sold C | Halls A | Drawn A | Drawn B | Drawn C | PUE A | PUE B | PUE C | Tariff | Price A | Price B | Price C | Rent A | Rent B | Rent C | Cross-connects | Services | IT MWh A | IT MWh B | IT MWh C | Fac MWh A | Fac MWh B | Fac MWh C | Cost A | Cost B | Cost C | Billed A | Billed B | Billed C | Margin A | Margin B | Margin C | Churn A | Gross A | Gross B | Commission | Water m3
1 | 1 | 0.041667 | 1925 | 3125 | 6000 | 1 | 1058.75 | 2031.25 | 4500 | 1.4525 | 1.4954 | 1.2067 | 74 | 195 | 135 | 118 | 375375 | 421875 | 708000 | 17325 | 7575 | 772.8875 | 1482.8125 | 3285 | 1122.6305 | 2217.375 | 3963.9 | 83074.657 | 164085.75 | 293328.6 | 88650.1962 | 166519.8438 | 293328.6 | 5575.5393 | 2434.0938 | 0 | 10.8 | 135.8 | 125 | 43356 | 2974.02
2 | 1 | 0.125 | 2175 | 3375 | 6000 | 1 | 1196.25 | 2193.75 | 4500 | 1.4281 | 1.4735 | 1.2067 | 74 | 195 | 135 | 118 | 424125 | 455625 | 708000 | 19575 | 8325 | 873.2625 | 1601.4375 | 3285 | 1247.0955 | 2359.725 | 3963.9 | 92285.067 | 174619.65 | 293328.6 | 100163.2088 | 179841.4312 | 293328.6 | 7878.1418 | 5221.7812 | 0 | 11.55 | 261.55 | 250 | 84752.25 | 3214.92
3 | 1 | 0.20833 | 2425 | 3625 | 6000 | 1 | 1333.75 | 2356.25 | 4500 | 1.4087 | 1.4546 | 1.2067 | 74 | 195 | 135 | 118 | 472875 | 489375 | 708000 | 21825 | 9075 | 973.6375 | 1720.0625 | 3285 | 1371.5605 | 2502.075 | 3963.9 | 101495.477 | 185153.55 | 293328.6 | 111676.2213 | 193163.0187 | 293328.6 | 10180.7442 | 8009.4688 | 0 | 13.05 | 263.05 | 250 | 85044.75 | 3455.82
4 | 1 | 0.29167 | 2675 | 3875 | 6000 | 1 | 1471.25 | 2518.75 | 4500 | 1.3929 | 1.4382 | 1.2067 | 74 | 195 | 135 | 118 | 521625 | 523125 | 708000 | 24075 | 9825 | 1074.0125 | 1838.6875 | 3285 | 1496.0255 | 2644.425 | 3963.9 | 110705.887 | 195687.45 | 293328.6 | 123189.2337 | 204880.8875 | 293328.6 | 12483.3468 | 9193.4375 | 0 | 14.55 | 264.55 | 250 | 85337.25 | 3696.72
5 | 1 | 0.375 | 2925 | 4125 | 6000 | 1 | 1608.75 | 2681.25 | 4500 | 1.3799 | 1.4238 | 1.2067 | 74 | 195 | 135 | 118 | 570375 | 556875 | 708000 | 26325 | 10575 | 1174.3875 | 1957.3125 | 3285 | 1620.4905 | 2786.775 | 3963.9 | 119916.297 | 206221.35 | 293328.6 | 134702.2462 | 216007.9125 | 293328.6 | 14785.9492 | 9786.5625 | 0 | 16.05 | 266.05 | 250 | 85629.75 | 3937.62
6 | 1 | 0.45833 | 3175 | 4375 | 6000 | 2 | 1746.25 | 2843.75 | 4500 | 1.4977 | 1.411 | 1.2067 | 74 | 195 | 135 | 118 | 619125 | 590625 | 708000 | 28575 | 11325 | 1274.7625 | 2075.9375 | 3285 | 1909.2055 | 2929.125 | 3963.9 | 141281.207 | 216755.25 | 293328.6 | 146215.2588 | 227134.9375 | 293328.6 | 4934.0518 | 10379.6875 | 0 | 17.55 | 267.55 | 250 | 85922.25 | 4178.52
7 | 1 | 0.54167 | 3425 | 4625 | 6000 | 2 | 1883.75 | 3006.25 | 4500 | 1.4789 | 1.3996 | 1.2067 | 74 | 195 | 135 | 118 | 667875 | 624375 | 708000 | 30825 | 12075 | 1375.1375 | 2194.5625 | 3285 | 2033.6705 | 3071.475 | 3963.9 | 150491.617 | 227289.15 | 293328.6 | 157728.2712 | 238261.9625 | 293328.6 | 7236.6543 | 10972.8125 | 0 | 19.05 | 269.05 | 250 | 86214.75 | 4419.42
8 | 1 | 0.625 | 3675 | 4875 | 6000 | 2 | 2021.25 | 3168.75 | 4500 | 1.4626 | 1.3893 | 1.2067 | 74 | 195 | 135 | 118 | 716625 | 658125 | 708000 | 33075 | 12825 | 1475.5125 | 2313.1875 | 3285 | 2158.1355 | 3213.825 | 3963.9 | 159702.027 | 237823.05 | 293328.6 | 169241.2838 | 249388.9875 | 293328.6 | 9539.2568 | 11565.9375 | 0 | 20.55 | 270.55 | 250 | 86507.25 | 4660.32
9 | 1 | 0.70833 | 3925 | 5125 | 6000 | 2 | 2158.75 | 3331.25 | 4500 | 1.4485 | 1.3801 | 1.2067 | 74 | 195 | 135 | 118 | 765375 | 691875 | 708000 | 35325 | 13575 | 1575.8875 | 2431.8125 | 3285 | 2282.6005 | 3356.175 | 3963.9 | 168912.437 | 248356.95 | 293328.6 | 180754.2963 | 260516.0125 | 293328.6 | 11841.8592 | 12159.0625 | 0 | 22.05 | 272.05 | 250 | 86799.75 | 4901.22
10 | 1 | 0.79167 | 4175 | 5375 | 6000 | 2 | 2296.25 | 3493.75 | 4500 | 1.436 | 1.3717 | 1.2067 | 74 | 195 | 135 | 118 | 814125 | 725625 | 708000 | 37575 | 14325 | 1676.2625 | 2550.4375 | 3285 | 2407.0655 | 3498.525 | 3963.9 | 178122.847 | 258890.85 | 293328.6 | 192267.3087 | 271643.0375 | 293328.6 | 14144.4618 | 12752.1875 | 0 | 23.55 | 273.55 | 250 | 87092.25 | 5142.12
11 | 1 | 0.875 | 4425 | 5625 | 6000 | 2 | 2433.75 | 3656.25 | 4500 | 1.4249 | 1.3641 | 1.2067 | 74 | 195 | 135 | 118 | 862875 | 759375 | 708000 | 39825 | 15075 | 1776.6375 | 2669.0625 | 3285 | 2531.5305 | 3640.875 | 3963.9 | 187333.257 | 269424.75 | 293328.6 | 203780.3213 | 282770.0625 | 293328.6 | 16447.0642 | 13345.3125 | 0 | 25.05 | 275.05 | 250 | 87384.75 | 5383.02
12 | 1 | 0.95833 | 4675 | 5875 | 6000 | 2 | 2571.25 | 3818.75 | 4500 | 1.415 | 1.3571 | 1.2067 | 74 | 195 | 135 | 118 | 911625 | 793125 | 708000 | 42075 | 15825 | 1877.0125 | 2787.6875 | 3285 | 2655.9955 | 3783.225 | 3963.9 | 196543.667 | 279958.65 | 293328.6 | 215293.3337 | 293897.0875 | 293328.6 | 18749.6668 | 13938.4375 | 0 | 26.55 | 276.55 | 250 | 87677.25 | 5623.92
13 | 2 | 0.041667 | 4925 | 6125 | 9000 | 2 | 2708.75 | 3981.25 | 6750 | 1.4061 | 1.3507 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 989186.25 | 851681.25 | 1088550 | 44325 | 16575 | 1977.3875 | 2906.3125 | 4927.5 | 2780.4605 | 3925.575 | 5836.35 | 211926.6993 | 299207.3265 | 444846.597 | 233610.5366 | 313738.889 | 444846.597 | 21683.8373 | 14531.5625 | 0 | 28.05 | 278.05 | 250 | 90608.8425 | 6111.195
14 | 2 | 0.125 | 5175 | 6375 | 9000 | 2 | 2846.25 | 4143.75 | 6750 | 1.3981 | 1.3448 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1039398.75 | 886443.75 | 1088550 | 46575 | 17325 | 2077.7625 | 3024.9375 | 4927.5 | 2904.9255 | 4067.925 | 5836.35 | 221413.4216 | 310057.2435 | 444846.597 | 245468.9395 | 325181.931 | 444846.597 | 24055.5179 | 15124.6875 | 0 | 29.55 | 279.55 | 250 | 90910.1175 | 6352.095
15 | 2 | 0.20833 | 5425 | 6625 | 9000 | 2 | 2983.75 | 4306.25 | 6750 | 1.3908 | 1.3393 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1089611.25 | 921206.25 | 1088550 | 48825 | 18075 | 2178.1375 | 3143.5625 | 4927.5 | 3029.3905 | 4210.275 | 5836.35 | 230900.1439 | 320907.1605 | 444846.597 | 257327.3424 | 336624.973 | 444846.597 | 26427.1985 | 15717.8125 | 0 | 31.05 | 281.05 | 250 | 91211.3925 | 6592.995
16 | 2 | 0.29167 | 5675 | 6875 | 9000 | 2 | 3121.25 | 4468.75 | 6750 | 1.3842 | 1.3343 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1139823.75 | 955968.75 | 1088550 | 51075 | 18825 | 2278.5125 | 3262.1875 | 4927.5 | 3153.8555 | 4352.625 | 5836.35 | 240386.8662 | 331757.0775 | 444846.597 | 269185.7453 | 348068.015 | 444846.597 | 28798.8791 | 16310.9375 | 0 | 32.55 | 282.55 | 250 | 91512.6675 | 6833.895
17 | 2 | 0.375 | 5925 | 7125 | 9000 | 2 | 3258.75 | 4631.25 | 6750 | 1.3781 | 1.3296 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1190036.25 | 990731.25 | 1088550 | 53325 | 19575 | 2378.8875 | 3380.8125 | 4927.5 | 3278.3205 | 4494.975 | 5836.35 | 249873.5885 | 342606.9945 | 444846.597 | 281044.1481 | 359511.057 | 444846.597 | 31170.5596 | 16904.0625 | 0 | 34.05 | 284.05 | 250 | 91813.9425 | 7074.795
18 | 2 | 0.45833 | 6175 | 7375 | 9000 | 3 | 3396.25 | 4793.75 | 6750 | 1.4387 | 1.3252 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1240248.75 | 1025493.75 | 1088550 | 55575 | 20325 | 2479.2625 | 3499.4375 | 4927.5 | 3567.0355 | 4637.325 | 5836.35 | 271879.4458 | 353456.9115 | 444846.597 | 292902.551 | 370954.099 | 444846.597 | 21023.1052 | 17497.1875 | 0 | 35.55 | 285.55 | 250 | 92115.2175 | 7315.695
19 | 2 | 0.54167 | 6425 | 7625 | 9000 | 3 | 3533.75 | 4956.25 | 6750 | 1.431 | 1.3211 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1290461.25 | 1060256.25 | 1088550 | 57825 | 21075 | 2579.6375 | 3618.0625 | 4927.5 | 3691.5005 | 4779.675 | 5836.35 | 281366.1681 | 364306.8285 | 444846.597 | 304760.9539 | 382397.141 | 444846.597 | 23394.7858 | 18090.3125 | 0 | 37.05 | 287.05 | 250 | 92416.4925 | 7556.595
20 | 2 | 0.625 | 6675 | 7875 | 9000 | 3 | 3671.25 | 5118.75 | 6750 | 1.4239 | 1.3172 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1340673.75 | 1095018.75 | 1088550 | 60075 | 21825 | 2680.0125 | 3736.6875 | 4927.5 | 3815.9655 | 4922.025 | 5836.35 | 290852.8904 | 375156.7455 | 444846.597 | 316619.3568 | 393840.183 | 444846.597 | 25766.4664 | 18683.4375 | 0 | 38.55 | 288.55 | 250 | 92717.7675 | 7797.495
21 | 2 | 0.70833 | 6925 | 8125 | 9000 | 3 | 3808.75 | 5281.25 | 6750 | 1.4172 | 1.3136 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1390886.25 | 1129781.25 | 1088550 | 62325 | 22575 | 2780.3875 | 3855.3125 | 4927.5 | 3940.4305 | 5064.375 | 5836.35 | 300339.6127 | 386006.6625 | 444846.597 | 328477.7596 | 405283.225 | 444846.597 | 28138.1469 | 19276.5625 | 0 | 40.05 | 290.05 | 250 | 93019.0425 | 8038.395
22 | 2 | 0.79167 | 7175 | 8375 | 9000 | 3 | 3946.25 | 5443.75 | 6750 | 1.411 | 1.3102 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1441098.75 | 1164543.75 | 1088550 | 64575 | 23325 | 2880.7625 | 3973.9375 | 4927.5 | 4064.8955 | 5206.725 | 5836.35 | 309826.335 | 396856.5795 | 444846.597 | 340336.1625 | 416726.267 | 444846.597 | 30509.8275 | 19869.6875 | 0 | 41.55 | 291.55 | 250 | 93320.3175 | 8279.295
23 | 2 | 0.875 | 7425 | 8625 | 9000 | 3 | 4083.75 | 5606.25 | 6750 | 1.4053 | 1.307 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1491311.25 | 1199306.25 | 1088550 | 66825 | 24075 | 2981.1375 | 4092.5625 | 4927.5 | 4189.3605 | 5349.075 | 5836.35 | 319313.0573 | 407706.4965 | 444846.597 | 352194.5654 | 428169.309 | 444846.597 | 32881.5081 | 20462.8125 | 0 | 43.05 | 293.05 | 250 | 93621.5925 | 8520.195
24 | 2 | 0.95833 | 7675 | 8875 | 9000 | 3 | 4221.25 | 5768.75 | 6750 | 1.3999 | 1.304 | 1.1844 | 76.22 | 200.85 | 139.05 | 120.95 | 1541523.75 | 1234068.75 | 1088550 | 69075 | 24825 | 3081.5125 | 4211.1875 | 4927.5 | 4313.8255 | 5491.425 | 5836.35 | 328799.7796 | 418556.4135 | 444846.597 | 364052.9683 | 439612.351 | 444846.597 | 35253.1887 | 21055.9375 | 0 | 44.55 | 294.55 | 250 | 93922.8675 | 8761.095
25 | 3 | 0.041667 | 7875 | 9062.5 | 12000 | 3 | 4331.25 | 5890.625 | 9000 | 1.3958 | 1.3019 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1629144.5625 | 1297944.8438 | 1487685 | 70875 | 25406.25 | 3161.8125 | 4300.1562 | 6570 | 4413.3975 | 5598.1875 | 7708.8 | 346480.8322 | 439494.6668 | 605191.6781 | 384745.8813 | 460995.448 | 605191.6781 | 38265.0491 | 21500.7812 | 0 | 46.05 | 246.05 | 187.5 | 77755.748 | 9193.6656
26 | 3 | 0.125 | 8025 | 9187.5 | 12000 | 3 | 4413.75 | 5971.875 | 9000 | 1.3929 | 1.3005 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1660175.8875 | 1315847.5312 | 1487685 | 72225 | 25818.75 | 3222.0375 | 4359.4688 | 6570 | 4488.0765 | 5669.3625 | 7708.8 | 352343.6266 | 445082.374 | 605191.6781 | 392074.3743 | 466879.7178 | 605191.6781 | 39730.7477 | 21797.3438 | 0 | 47.25 | 197.25 | 125 | 58708.8799 | 9325.1569
27 | 3 | 0.20833 | 8175 | 9312.5 | 12000 | 3 | 4496.25 | 6053.125 | 9000 | 1.3901 | 1.2991 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1691207.2125 | 1333750.2188 | 1487685 | 73575 | 26231.25 | 3282.2625 | 4418.7812 | 6570 | 4562.7555 | 5740.5375 | 7708.8 | 358206.4209 | 450670.0813 | 605191.6781 | 399402.8672 | 472763.9875 | 605191.6781 | 41196.4463 | 22093.9062 | 0 | 48.15 | 198.15 | 125 | 58895.0678 | 9456.6481
28 | 3 | 0.29167 | 8325 | 9437.5 | 12000 | 3 | 4578.75 | 6134.375 | 9000 | 1.3874 | 1.2978 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1722238.5375 | 1351652.9062 | 1487685 | 74925 | 26643.75 | 3342.4875 | 4478.0938 | 6570 | 4637.4345 | 5811.7125 | 7708.8 | 364069.2153 | 456257.7886 | 605191.6781 | 406731.3602 | 478648.2573 | 605191.6781 | 42662.1449 | 22390.4688 | 0 | 49.05 | 199.05 | 125 | 59081.2558 | 9588.1394
29 | 3 | 0.375 | 8475 | 9562.5 | 12000 | 3 | 4661.25 | 6215.625 | 9000 | 1.3848 | 1.2965 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1753269.8625 | 1369555.5938 | 1487685 | 76275 | 27056.25 | 3402.7125 | 4537.4062 | 6570 | 4712.1135 | 5882.8875 | 7708.8 | 369932.0097 | 461845.4958 | 605191.6781 | 414059.8532 | 484532.5271 | 605191.6781 | 44127.8435 | 22687.0312 | 0 | 49.95 | 199.95 | 125 | 59267.4437 | 9719.6306
30 | 3 | 0.45833 | 8625 | 9687.5 | 12000 | 3 | 4743.75 | 6296.875 | 9000 | 1.3823 | 1.2953 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1784301.1875 | 1387458.2812 | 1487685 | 77625 | 27468.75 | 3462.9375 | 4596.7188 | 6570 | 4786.7925 | 5954.0625 | 7708.8 | 375794.8041 | 467433.2031 | 605191.6781 | 421388.3462 | 490416.7968 | 605191.6781 | 45593.5421 | 22983.5938 | 0 | 50.85 | 200.85 | 125 | 59453.6317 | 9851.1219
31 | 3 | 0.54167 | 8775 | 9812.5 | 12000 | 3 | 4826.25 | 6378.125 | 9000 | 1.3799 | 1.2941 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1815332.5125 | 1405360.9688 | 1487685 | 78975 | 27881.25 | 3523.1625 | 4656.0312 | 6570 | 4861.4715 | 6025.2375 | 7708.8 | 381657.5985 | 473020.9103 | 605191.6781 | 428716.8391 | 496301.0666 | 605191.6781 | 47059.2407 | 23280.1562 | 0 | 51.75 | 201.75 | 125 | 59639.8196 | 9982.6131
32 | 3 | 0.625 | 8925 | 9937.5 | 12000 | 3 | 4908.75 | 6459.375 | 9000 | 1.3775 | 1.2929 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1846363.8375 | 1423263.6562 | 1487685 | 80325 | 28293.75 | 3583.3875 | 4715.3438 | 6570 | 4936.1505 | 6096.4125 | 7708.8 | 387520.3928 | 478608.6176 | 605191.6781 | 436045.3321 | 502185.3363 | 605191.6781 | 48524.9393 | 23576.7188 | 0 | 52.65 | 202.65 | 125 | 59826.0076 | 10114.1044
33 | 3 | 0.70833 | 9075 | 10062.5 | 12000 | 4 | 4991.25 | 6540.625 | 9000 | 1.4203 | 1.2917 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1877395.1625 | 1441166.3438 | 1487685 | 81675 | 28706.25 | 3643.6125 | 4774.6562 | 6570 | 5175.0795 | 6167.5875 | 7708.8 | 406277.8963 | 484196.3248 | 605191.6781 | 443373.8251 | 508069.6061 | 605191.6781 | 37095.9288 | 23873.2812 | 0 | 53.55 | 203.55 | 125 | 60012.1955 | 10245.5956
34 | 3 | 0.79167 | 9225 | 10187.5 | 12000 | 4 | 5073.75 | 6621.875 | 9000 | 1.4174 | 1.2906 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1908426.4875 | 1459069.0312 | 1487685 | 83025 | 29118.75 | 3703.8375 | 4833.9688 | 6570 | 5249.7585 | 6238.7625 | 7708.8 | 412140.6907 | 489784.0321 | 605191.6781 | 450702.3181 | 513953.8758 | 605191.6781 | 38561.6274 | 24169.8438 | 0 | 54.45 | 204.45 | 125 | 60198.3835 | 10377.0869
35 | 3 | 0.875 | 9375 | 10312.5 | 12000 | 4 | 5156.25 | 6703.125 | 9000 | 1.4145 | 1.2895 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1939457.8125 | 1476971.7188 | 1487685 | 84375 | 29531.25 | 3764.0625 | 4893.2812 | 6570 | 5324.4375 | 6309.9375 | 7708.8 | 418003.485 | 495371.7393 | 605191.6781 | 458030.811 | 519838.1456 | 605191.6781 | 40027.326 | 24466.4062 | 0 | 55.35 | 205.35 | 125 | 60384.5714 | 10508.5781
36 | 3 | 0.95833 | 9525 | 10437.5 | 12000 | 4 | 5238.75 | 6784.375 | 9000 | 1.4118 | 1.2884 | 1.1733 | 78.5066 | 206.8755 | 143.2215 | 123.9737 | 1970489.1375 | 1494874.4062 | 1487685 | 85725 | 29943.75 | 3824.2875 | 4952.5938 | 6570 | 5399.1165 | 6381.1125 | 7708.8 | 423866.2794 | 500959.4466 | 605191.6781 | 465359.304 | 525722.4153 | 605191.6781 | 41493.0246 | 24762.9688 | 0 | 56.25 | 206.25 | 125 | 60570.7594 | 10640.0694

## Staffing
Staffing and operating models (Chapter 2)
Role | FTE | Loaded cost ($k) | Cost year 1 ($) | Group
Site director | 1 | 245 | 245000 | core
Operations manager | 1 | 180 | 180000 | core
Shift leads (one 24x7 seat) | 5 | 150 | 750000 | other
Critical facility technicians (two 24x7 seats) | 10 | 118 | 1180000 | technician
Day engineers: electrical, mechanical, controls | 3 | 145 | 435000 | other
Maintenance planner | 1 | 110 | 110000 | other
EHS and compliance lead | 1 | 125 | 125000 | core
Customer operations technicians (one 24x7 seat) | 5 | 95 | 475000 | technician
Customer operations manager | 1 | 140 | 140000 | core
TOTAL | 28 |  | 3640000
FTE per round-the-clock seat | 4.8667
FTE per design MW | 0.77778
Staff cost per design kW-month | 8.4259
Security, year 1 ($) | 665760
Retained core (in-house leadership) ($) | 690000
Vendor cost factor | 97%
Vendor fee | 15%
In-house model ($) | 3640000
Outsourced model ($) | 3980725
Hybrid model, technicians outsourced ($) | 3831152.5

## Power_SLA
Power, generators, circuits and the SLA (Chapters 3, 4, 7)
NINES
Three nines: minutes a year | 525.6
Four nines: minutes a year | 52.56
Five nines: minutes a year | 5.256
Six nines: minutes a year | 0.5256
GENERATOR TESTING
Monthly runs: gallons a year | 9450
Annual load bank: gallons a year | 13500
Total test fuel: gallons a year | 22950
Test fuel cost, year 1 ($) | 87210
Scope 1 from testing (tCO2) | 234.3195
FUEL AUTONOMY
Burn rate at design load, one building (gallons per hour) | 1157.1429
Fuel for the autonomy period, one building (gallons) | 55542.8571
CIRCUITS
208 V three-phase 30 A at 80 percent (kW) | 8.6464
208 V three-phase 60 A at 80 percent (kW) | 17.2928
INCIDENT, MONTH 7 (CHAPTER 7)
MRC of the affected customers ($) | 118950
Credit tier (share of MRC) | 10%
Credit ($) | 11895
Sold kW at the time (campus) | 14050
Campus kW-weighted availability, month | 100%
Campus kW-weighted availability, year | 100%
Affected customer availability, month | 99.97%
Affected customer availability, year | 100%

## Annual
Three-year budget, loan and reporting measures (Chapters 11, 13, 15)
Amounts in $ unless stated. Columns B to D are years 1 to 3.
Line | Year 1 | Year 2 | Year 3
Rent, Building A (retail) | 7722000 | 15184260 | 21597802.2
Rent, Building B (wholesale) | 7290000 | 12514500 | 16756915.5
Rent, Building C (hyperscale) | 8496000 | 13062600 | 17852220
Cross-connects | 356400 | 680400 | 939600
Remote hands and services | 140400 | 248400 | 332100
RECURRING REVENUE | 24004800 | 41690160 | 57478637.7
Energy billed to customers | 8127629.5613 | 13444247.6334 | 18283238.4291
TOTAL REVENUE | 32132429.5613 | 55134407.6334 | 75761876.1291
Energy bought from the utility | 7874074.044 | 12901619.6125 | 17501318.0687
Staff | 3640000 | 3767400 | 3899259
Security (contracted) | 665760 | 689061.6 | 713178.756
Maintenance contracts | 1749000 | 1801470 | 1855514.1
Repairs and consumables | 450000 | 463500 | 477405
Generator test fuel | 87210 | 89826.3 | 92521.089
Insurance and property tax, gross | 3300000 | 3399000 | 3500970
Recovered from Building C | 1100000 | 1133000 | 1166990
Audits | 160000 | 164800 | 169744
Water and sewer | 412701.12 | 735286.0176 | 1009997.2542
Platform management fee | 720144 | 1250704.8 | 1724359.131
Sales commissions | 991718.25 | 1107190.26 | 733793.7639
OPERATING COSTS EXCLUDING ENERGY | 11076533.37 | 12335238.9776 | 13009752.0941
SITE EBITDA | 13181822.1473 | 29897549.0433 | 45250805.9663
Energy margin, Building A | 133796.736 | 329103.0209 | 504337.8604
Energy margin, Building B | 119758.7812 | 213525 | 277582.5
Energy margin, Building C | 0 | 0 | 0
Net revenue (recurring plus energy margin) | 24258355.5173 | 42232788.0209 | 58260558.0604
EBITDA margin on total revenue | 41.02% | 54.23% | 59.73%
EBITDA margin on net revenue | 54.34% | 70.79% | 77.67%
Fixed costs (staff, security, contracts, repairs, fuel, net tax, audits) | 8951970 | 9242057.9 | 9541601.945
Average sold kW, A | 3300 | 6300 | 8700
Average sold kW, B | 4500 | 7500 | 9750
Average sold kW, C | 6000 | 9000 | 12000
EBITDA per design MW | 366161.7263 | 830487.4734 | 1256966.8324
EBITDA per sold MW | 955204.5034 | 1311296.0107 | 1486069.1615
IT MWh, A | 15899.4 | 30353.4 | 41916.6
Facility MWh, A | 22836.006 | 42729.966 | 58546.584
IT MWh, B | 25623 | 42705 | 55516.5
Facility MWh, B | 36003.6 | 56502 | 71875.8
IT MWh, C | 39420 | 59130 | 78840
Facility MWh, C | 47566.8 | 70036.2 | 92505.6
PUE, Building A | 1.4363 | 1.4077 | 1.3967
PUE, Building B | 1.4051 | 1.3231 | 1.2947
PUE, Building C | 1.2067 | 1.1844 | 1.1733
PUE, campus | 1.3146 | 1.2805 | 1.2647
Water (cubic meters) | 51587.64 | 89233.74 | 119002.41
WUE, campus (liters per kWh of IT energy) | 0.63734 | 0.67505 | 0.6751
Scope 2, location-based (tCO2e) | 40434.4343 | 64321.9031 | 84712.6339
Scope 2, market-based (tCO2e) | 16173.7737 | 25728.7612 | 33885.0536
Lifecycle reserve | 1260000 | 1260000 | 1260000
CASH FLOW AVAILABLE FOR DEBT SERVICE | 11921822.1473 | 28637549.0433 | 43990805.9663
Interest | 19200000 | 19200000 | 19200000
Principal | 0 | 0 | 9000000
Debt service | 19200000 | 19200000 | 28200000
DSCR | 0.62093 | 1.4915 | 1.56
Gross kW sold, A | 3095.35 | 3435.6 | 2465.3
kW churned, A | 220.35 | 435.6 | 615.3
Gross kW sold, B | 2875 | 3000 | 1562.5
Interest reserve needed in year 1 (debt service less CFADS) | 7278177.8527
Year 3: recurring revenue cut to lock-up ($) | 9011140.1715
Year 3: same as share of recurring revenue | 15.68%
Year 3: recurring revenue cut to default ($) | 13371964.9137
Year 3: same as share of recurring revenue | 23.26%
Year 1 net revenue per sold kW-month | 146.4877
Contribution after the management fee | 142.093
Fixed costs and water, year 1 | 9364671.12
EBITDA breakeven, sold kW (year 1) | 5492.1011
Sold kW to cover fixed costs, lifecycle and interest (year 1) | 17491.2827
Building C's share of year-3 recurring revenue | 31.06%
Year-1 value of conditioning halls as needed (energy margin) | 352480.5

## Cooling
Cooling levers in Building A (Chapter 5)
Halls conditioned as needed (base), all four halls conditioned, and warmer supply air.
Measure | Base (as needed) | All four halls | Warmer air
PUE A, year 1 | 1.4363 | 1.7359 | 1.4063
PUE A, year 2 | 1.4077 | 1.4997 | 1.3777
PUE A, year 3 | 1.3967 | 1.4281 | 1.3667
Energy margin A, year 1 | 133796.736 | -218683.764 | 169093.404
Energy margin A, year 2 | 329103.0209 | 116277.7259 | 398509.1053
Energy margin A, year 3 | 504337.8604 | 401180.188 | 603059.7529
Year-1 energy margin: base / all halls | 133796.736 | -218683.764
Month-1 PUE A, base | 1.4525
Month-1 PUE A, all four halls | 2.0901
Hall breakeven: drawn kW per conditioned hall | 725.8065
Hall breakeven: sold kW per conditioned hall | 1319.6481
|  |  |  | Month | PUE all halls | PUE warmer | Fac MWh all | Margin all | Fac MWh warm | Margin warm
|  |  |  | 1 | 2.0901 | 1.4225 | 1615.3805 | -30887.9607 | 1099.4439 | 7291.3495
|  |  |  | 2 | 1.9924 | 1.3981 | 1739.8455 | -28585.3583 | 1220.8976 | 9816.7845
|  |  |  | 3 | 1.9148 | 1.3787 | 1864.3105 | -26282.7558 | 1342.3514 | 12342.2195
|  |  |  | 4 | 1.8517 | 1.3629 | 1988.7755 | -23980.1532 | 1463.8051 | 14867.6545
|  |  |  | 5 | 1.7994 | 1.3499 | 2113.2405 | -21677.5507 | 1585.2589 | 17393.0895
|  |  |  | 6 | 1.7554 | 1.4677 | 2237.7055 | -19374.9483 | 1870.9626 | 7764.0245
|  |  |  | 7 | 1.7178 | 1.4489 | 2362.1705 | -17072.3458 | 1992.4164 | 10289.4595
|  |  |  | 8 | 1.6853 | 1.4326 | 2486.6355 | -14769.7432 | 2113.8701 | 12814.8945
|  |  |  | 9 | 1.6569 | 1.4185 | 2611.1005 | -12467.1408 | 2235.3239 | 15340.3295
|  |  |  | 10 | 1.6319 | 1.406 | 2735.5655 | -10164.5382 | 2356.7776 | 17865.7645
|  |  |  | 11 | 1.6098 | 1.3949 | 2860.0305 | -7861.9357 | 2478.2314 | 20391.1995
|  |  |  | 12 | 1.59 | 1.385 | 2984.4955 | -5559.3333 | 2599.6851 | 22916.6345
|  |  |  | 13 | 1.5723 | 1.3761 | 3108.9605 | -3354.4327 | 2721.1389 | 26205.3316
|  |  |  | 14 | 1.5562 | 1.3681 | 3233.4255 | -982.7521 | 2842.5926 | 28806.5296
|  |  |  | 15 | 1.5416 | 1.3608 | 3357.8905 | 1388.9285 | 2964.0464 | 31407.7277
|  |  |  | 16 | 1.5283 | 1.3542 | 3482.3555 | 3760.6091 | 3085.5001 | 34008.9257
|  |  |  | 17 | 1.5162 | 1.3481 | 3606.8205 | 6132.2896 | 3206.9539 | 36610.1238
|  |  |  | 18 | 1.505 | 1.4087 | 3731.2855 | 8503.9702 | 3492.6576 | 26692.1868
|  |  |  | 19 | 1.4947 | 1.401 | 3855.7505 | 10875.6508 | 3614.1114 | 29293.3849
|  |  |  | 20 | 1.4851 | 1.3939 | 3980.2155 | 13247.3314 | 3735.5651 | 31894.5829
|  |  |  | 21 | 1.4763 | 1.3872 | 4104.6805 | 15619.0119 | 3857.0189 | 34495.781
|  |  |  | 22 | 1.4681 | 1.381 | 4229.1455 | 17990.6925 | 3978.4726 | 37096.979
|  |  |  | 23 | 1.4604 | 1.3753 | 4353.6105 | 20362.3731 | 4099.9264 | 39698.1771
|  |  |  | 24 | 1.4532 | 1.3699 | 4478.0755 | 22734.0537 | 4221.3801 | 42299.3751
|  |  |  | 25 | 1.4478 | 1.3658 | 4577.6475 | 25370.3401 | 4318.5431 | 45711.7436
|  |  |  | 26 | 1.4439 | 1.3629 | 4652.3265 | 26836.0387 | 4391.4154 | 47319.284
|  |  |  | 27 | 1.4402 | 1.3601 | 4727.0055 | 28301.7372 | 4464.2876 | 48926.8244
|  |  |  | 28 | 1.4366 | 1.3574 | 4801.6845 | 29767.4358 | 4537.1599 | 50534.3648
|  |  |  | 29 | 1.4331 | 1.3548 | 4876.3635 | 31233.1344 | 4610.0321 | 52141.9052
|  |  |  | 30 | 1.4297 | 1.3523 | 4951.0425 | 32698.833 | 4682.9044 | 53749.4456
|  |  |  | 31 | 1.4265 | 1.3499 | 5025.7215 | 34164.5316 | 4755.7766 | 55356.986
|  |  |  | 32 | 1.4233 | 1.3475 | 5100.4005 | 35630.2302 | 4828.6489 | 56964.5263
|  |  |  | 33 | 1.4203 | 1.3903 | 5175.0795 | 37095.9288 | 5065.7711 | 45677.3577
|  |  |  | 34 | 1.4174 | 1.3874 | 5249.7585 | 38561.6274 | 5138.6434 | 47284.8981
|  |  |  | 35 | 1.4145 | 1.3845 | 5324.4375 | 40027.326 | 5211.5156 | 48892.4385
|  |  |  | 36 | 1.4118 | 1.3818 | 5399.1165 | 41493.0246 | 5284.3879 | 50499.9789

## Maintenance
Preventive maintenance program (Chapter 6)
Asset family | Assets | Visits a year | Hours per visit | Crew | By | Work orders | Person-hours
Generators, monthly run and inspection | 21 | 12 | 1.5 | 2 | in-house | 252 | 756
Generators, annual load bank and service | 21 | 1 | 6 | 2 | vendor | 21 | 252
UPS modules | 48 | 2 | 3 | 2 | vendor | 96 | 576
Battery strings, impedance and visual | 96 | 4 | 1 | 1 | in-house | 384 | 384
Chillers | 12 | 4 | 6 | 2 | vendor | 48 | 576
CRAH units and fan walls | 120 | 4 | 1.5 | 1 | in-house | 480 | 720
Pumps | 36 | 2 | 2 | 1 | in-house | 72 | 144
Medium-voltage switchgear | 9 | 1 | 16 | 3 | vendor | 9 | 432
Switchboards and PDUs, infrared scan | 180 | 1 | 0.5 | 2 | in-house | 180 | 180
Transfer scheme functional tests | 6 | 2 | 8 | 3 | in-house | 12 | 288
Fire detection and suppression zones | 24 | 2 | 2 | 2 | vendor | 48 | 192
Cooling towers and dry coolers | 18 | 4 | 3 | 2 | in-house | 72 | 432
Work orders a year | 1674
Work orders per working day (250 days) | 6.696
Person-hours a year | 4932
In-house person-hours | 2904
Vendor person-hours | 2028
Productive hours of the three day engineers | 5400
In-house PM share of day-engineer hours | 53.78%
Maintainable assets (generators counted once) | 570

## Capacity
Capacity management (Chapter 10)
OVERSUBSCRIPTION, BUILDING A
Sell ratio | 110%
Sold kW | 13200
Breakeven draw (share of commitments) | 90.91%
Draw (share of commitments) | Load (kW) | Share of design
55% | 7260 | 60.5%
70% | 9240 | 77%
85% | 11220 | 93.5%
95% | 12540 | 104.5%
UPS BLOCKS, BUILDING B
Block rating (kW) | 4000
Safe loading limit | 75%
Safe limit per block (kW) | 3000
Critical capacity, four blocks (kW) | 12000
Block | Load at contracted capacity (kW) | Headroom (kW) | After a 1,200 kW suite on B3 and B4
B1 | 3000 | 0 | 0
B2 | 2760 | 240 | 240
B3 | 2340 | 660 | 60
B4 | 2400 | 600 | 0
Sold (kW) | 10500
Unsold on paper (kW) | 1500
Blocks with 750 kW of headroom (a 1,500 kW suite needs two) | 0
Blocks with 600 kW of headroom (a 1,200 kW suite needs two) | 2
Stranded after a 1,200 kW suite on B3 and B4 (kW) | 300
Load on B3 and B4 with the suite at full load (kW) | 2940 | 3000
MONTH 30 SNAPSHOT
Sold kW, campus | 30312.5
Drawn kW, campus | 20040.625
Drawn as share of sold | 66.11%
Sold as share of design | 84.2%
Recurring revenue in month 30 | 4764538.2188

## Pricing
Price floor, energy structures and the hyperscale ramp (Chapters 8 and 9)
Build cost per kW | 11000
Capital charge per kW-month at the required yield | 82.5
Year-3 operating cost per design kW-month (excl. energy and commissions) | 28.4166
Price floor per kW-month | 110.9166
Per 1,000 MWh of IT energy at the year-1 tariff | Fixed multiplier | Fee pass-through
1.35 | 14800 | 5000
1.5 | 3700 | 5000
1.7 | -11100 | 5000
HYPERSCALE RAMP
Year-1 rent had 12 MW been billable from day one | 16992000
Rent given up by the ramp in years 1 and 2 | 12850200
Backlog in lease year 2 (annual rent of capacity signed, not billable) | 4354200

## Retrofit
Suite B8: air-cooled or liquid-cooled (Chapter 14)
Air-cooled price, year 3 ($ per kW-month) | 143.2215
Liquid-cooling capex | 3840000
Annual rent, air-cooled | 2062389.6
Annual rent, liquid-cooled | 2520000
Annuity factor (escalating rent, discounted) | 7.2053
PV of liquid rent lost to the works in year 1 | 1155963.3028
CASE 1: an air-cooled buyer exists
Annual increment (full year) | 457610.4
Additional capex | 3690000
Simple payback on a full year (years) | 8.0636
Ten-year NPV (with the works delay) | -1548764.4596
Liquid price for NPV zero | 190.942
CASE 2: no air-cooled buyer
Annual increment (full year) | 2520000
Capex | 3840000
Simple payback (years) | 1.5238
Ten-year NPV (with the works delay) | 13161275.0049

## Checks
The book's printed figures beside the live formulas (default inputs)
Figure | Printed in the book | Live formula | Status | Tolerance
Recurring revenue, year 1 ($m) | 24 | 24.0048 | OK | 0.005
Total revenue, year 1 ($m) | 32.13 | 32.1324 | OK | 0.005
Energy cost, year 1 ($m) | 7.87 | 7.8741 | OK | 0.005
Site EBITDA, year 1 ($m) | 13.18 | 13.1818 | OK | 0.005
Energy margin A, year 1 ($m) | 0.13 | 0.1338 | OK | 0.005
Energy margin B, year 1 ($m) | 0.12 | 0.11976 | OK | 0.005
PUE campus, year 1 | 1.31 | 1.3146 | OK | 0.005
PUE A, year 1 | 1.44 | 1.4363 | OK | 0.005
PUE B, year 1 | 1.41 | 1.4051 | OK | 0.005
PUE C, year 1 | 1.21 | 1.2067 | OK | 0.005
DSCR, year 1 | 0.62 | 0.62093 | OK | 0.005
EBITDA per design MW, year 1 ($m) | 0.37 | 0.36616 | OK | 0.005
Scope 2 location-based, year 1 (t) | 40434 | 40434.4343 | OK | 0.5
Water, year 1 (m3) | 51588 | 51587.64 | OK | 0.5
WUE campus, year 1 | 0.64 | 0.63734 | OK | 0.005
Recurring revenue, year 2 ($m) | 41.69 | 41.6902 | OK | 0.005
Total revenue, year 2 ($m) | 55.13 | 55.1344 | OK | 0.005
Energy cost, year 2 ($m) | 12.9 | 12.9016 | OK | 0.005
Site EBITDA, year 2 ($m) | 29.9 | 29.8975 | OK | 0.005
Energy margin A, year 2 ($m) | 0.33 | 0.3291 | OK | 0.005
Energy margin B, year 2 ($m) | 0.21 | 0.21352 | OK | 0.005
PUE campus, year 2 | 1.28 | 1.2805 | OK | 0.005
PUE A, year 2 | 1.41 | 1.4077 | OK | 0.005
PUE B, year 2 | 1.32 | 1.3231 | OK | 0.005
PUE C, year 2 | 1.18 | 1.1844 | OK | 0.005
DSCR, year 2 | 1.49 | 1.4915 | OK | 0.005
EBITDA per design MW, year 2 ($m) | 0.83 | 0.83049 | OK | 0.005
Scope 2 location-based, year 2 (t) | 64322 | 64321.9031 | OK | 0.5
Water, year 2 (m3) | 89234 | 89233.74 | OK | 0.5
WUE campus, year 2 | 0.68 | 0.67505 | OK | 0.005
Recurring revenue, year 3 ($m) | 57.48 | 57.4786 | OK | 0.005
Total revenue, year 3 ($m) | 75.76 | 75.7619 | OK | 0.005
Energy cost, year 3 ($m) | 17.5 | 17.5013 | OK | 0.005
Site EBITDA, year 3 ($m) | 45.25 | 45.2508 | OK | 0.005
Energy margin A, year 3 ($m) | 0.5 | 0.50434 | OK | 0.005
Energy margin B, year 3 ($m) | 0.28 | 0.27758 | OK | 0.005
PUE campus, year 3 | 1.26 | 1.2647 | OK | 0.005
PUE A, year 3 | 1.4 | 1.3967 | OK | 0.005
PUE B, year 3 | 1.29 | 1.2947 | OK | 0.005
PUE C, year 3 | 1.17 | 1.1733 | OK | 0.005
DSCR, year 3 | 1.56 | 1.56 | OK | 0.005
EBITDA per design MW, year 3 ($m) | 1.26 | 1.257 | OK | 0.005
Scope 2 location-based, year 3 (t) | 84713 | 84712.6339 | OK | 0.5
Water, year 3 (m3) | 119002 | 119002.41 | OK | 0.5
WUE campus, year 3 | 0.68 | 0.6751 | OK | 0.005
EBITDA margin on net revenue, year 3 | 0.777 | 77.67% | OK | 0.0005
Interest reserve, year 1 ($m) | 7.28 | 7.2782 | OK | 0.005
Year 3 cut to lock-up ($m) | 9.01 | 9.0111 | OK | 0.005
Year 3 cut to default ($m) | 13.37 | 13.372 | OK | 0.005
EBITDA breakeven, sold kW | 5492 | 5492.1011 | OK | 0.5
Sold kW to cover fixed, lifecycle, interest | 17491 | 17491.2827 | OK | 0.5
Building C share of year-3 recurring revenue | 0.311 | 31.06% | OK | 0.0005
Value of conditioning halls as needed, year 1 ($m) | 0.35 | 0.35248 | OK | 0.005
Month-1 PUE A, base | 1.45 | 1.4525 | OK | 0.005
Month-1 PUE A, all four halls | 2.09 | 2.0901 | OK | 0.005
Year-1 energy margin A, all halls ($m) | -0.22 | -0.21868 | OK | 0.005
Year-3 energy margin A, warmer air ($m) | 0.6 | 0.60306 | OK | 0.005
Hall breakeven, sold kW | 1320 | 1319.6481 | OK | 0.5
Staff cost, year 1 ($m) | 3.64 | 3.64 | OK | 0.005
Outsourced model ($m) | 3.98 | 3.9807 | OK | 0.005
Hybrid model ($m) | 3.83 | 3.8312 | OK | 0.005
FTE per 24x7 seat | 4.87 | 4.8667 | OK | 0.005
Five nines, minutes a year | 5.26 | 5.256 | OK | 0.005
Test fuel, gallons a year | 22950 | 22950 | OK | 0.5
Test fuel cost, year 1 ($) | 87210 | 87210 | OK | 0.5
Fuel for 48 hours, one building (gallons) | 55543 | 55542.8571 | OK | 0.5
Circuit 208 V 30 A (kW) | 8.65 | 8.6464 | OK | 0.005
Incident credit ($) | 11895 | 11895 | OK | 0.5
Campus availability in month 7 | 0.99999 | 100% | OK | 5e-08
PM work orders a year | 1674 | 1674 | OK | 0.5
PM person-hours a year | 4932 | 4932 | OK | 0.5
In-house PM share of day-engineer hours | 0.54 | 53.78% | OK | 0.005
Breakeven draw when 110 percent sold | 0.909 | 90.91% | OK | 0.0005
Stranded kW in Building B | 300 | 300 | OK | 0.5
Month 30 sold kW | 30312 | 30312.5 | OK | 0.5
Month 30 drawn kW | 20041 | 20040.625 | OK | 0.5
Month 30 recurring revenue ($m) | 4.76 | 4.7645 | OK | 0.005
Price floor ($ per kW-month) | 110.92 | 110.9166 | OK | 0.005
Fixed multiplier at PUE 1.70 ($) | -11100 | -11100 | OK | 0.5
Rent given up by the ramp ($m) | 12.85 | 12.8502 | OK | 0.005
Backlog, lease year 2 ($m) | 4.35 | 4.3542 | OK | 0.005
Retrofit case 1 NPV ($m) | -1.55 | -1.5488 | OK | 0.005
Retrofit case 1 payback (years) | 8.1 | 8.0636 | OK | 0.05
Retrofit case 2 NPV ($m) | 13.16 | 13.1613 | OK | 0.005
Retrofit breakeven price | 190.94 | 190.942 | OK | 0.005
Scope 1 from testing (t) | 234 | 234.3195 | OK | 0.5
RESULT |  |  | ALL CHECKS OK